## Summary
My Project Summary
1) Legend / Color Coding
YOU ONLY NEED TO FILL THE GREEN CELLS!
|  | : | Enter your own project facts and figures here
|  | : | Fixed numbers provided to you [you don't have to add anything to these cells]
|  | : | Automatically calculated figures [you don't have to add anything to these cells]
2) Project Short Description
The Joinery and Carpentry programs within the School of Construction and the Environment produce a significant amount of wood waste that needs to be trucked off of campus on a regular basis. This project is about installing a biomass boiler on campus to burn the wood waste and produce heat that will be both used to heat space in our buildings and heat domestic hot water. More details can be found in the detailed business case document.
3) My project Cost
Enter your details in the "My Project Cost" tab and final numbers will appear here.
a) Capital Cost
|  |  | Figure | Unit
|  | Total Capital Cost: | 548700 | $
b) Annual Operation and Maintenance Cost
|  |  | Figure | Unit
|  | Total Operation and Maintenance: | 10663.05 | $/yr
|  | c) Other costs | Figure | Unit
|  |  | 0 | $/yr
4) My project Savings
Enter your details in the "My Project Savings" tab and final numbers will appear here..
|  |  | Figure | Unit
|  | Electricity Savings: | 0 | $/yr
|  | Natural Gas Savings: | 40500 | $/yr
|  | Greenhouse Gas Emissions Savings: | 6250 | $/yr
|  | Water Savings: | 0 | $/yr
|  | Other Savings: | 12000 | $/yr
|  | Total Savings: | 58750 | $/yr
5) My Project financial analysis
a) Note to the applicant
It is recommended to run your numbers with both your optimistic and pessimistic scenarios to see how much your cost, savings and project value vary (in other words: it is recommended to perform a sensitivity analysis).
b) Questions
|  |  | Figure | Unit
|  | Are the Operation and Maintenance Cost and the savings occurring each and every year for the entire life of the project: | yes | yes or no
|  | What is the expected Life Span of your project: | 20 | yrs
c) Total project financial analysis (without external grants)
|  |  | Figure | Unit
|  | Simple payback [This is a checkpoint: Is my simple payback 5 yrs or less (threshold for loan eligibility)?] | 9.3396 | yrs
d) BCIT loan portion only
I.e.: if your project cannot payback for itself within five years as required by the BCIT Sustainability Revolving fund, you might want to consider securing external funding (e.g.: grants) and apply to the BCIT Sustainability Revolving Fund only for the portion than can be repaid within a five year period (total cost - grants).
|  |  | Figure | Unit
|  | Enter here the amount secured in grants (e.g.: from BC Hydro Power Smart incentives) | 250000 | $
|  |  | Figure | Unit
|  | Simple payback (BCIT loan portion only) [This is a checkpoint: Is my simple payback 5 yrs or less (threshold for loan eligibility)?] | 5.0843 | yrs
|  | Total Life Cycle Net Present Value [including external grants] | 346476.09 | $ | With discounted cash flow at 6% discount rate; over life of the project; all cost and revenues included. Refer to policy 1012 for more details.
6) Assumptions
|  |  | Figure | Unit
|  | Electrical Cost: | 0.068 | $/kWh
|  | Natural Gas Cost: | 9 | $/GJ
|  | Greenhouse Gas emissions Carbon offset cost: | 25 | $/tonne of CO2 equivalent
|  | Water cost: | 0.0015 | $/litre
|  | General Inflation: | 2% | %/yr
|  | Electricity cost inflation: | 6% | %/yr
|  | Natural Gas cost inflation: | 2% | %/yr
|  | Discount rate | 6% | %
Notes:
| 1) | A blank template will also be available.
| 2) | For more information, please contact BCIT's Energy and Sustainability manager or BCIT's Energy Specialist.

## My Project Cost
My Project Cost
Note the reader of this example:
This is an example only. The numbers in this section might not reflect perfectly a real life project. The intention is to illustrate what sort of calculations are needed to apply to the BCIT Sustainability revolving fund.
| : | Enter your own project figures here
| : | Automatically calculated figures
Option 1 Description
| Boiler size: | 250 kW
| Boiler make: | To be selected
| Heating load: | All campus - Connected to main line/central plant
| General Description: | Heat only Firebox boiler (self contained), fully automated, with silo, with chipper and with smoke stack and air particulate filter.
Capital Investment
CIVIL WORKS
|  | Foundation, incl. | for silo, container & stack |  | 20000
|  | excavation & dirt removal | incl. trench for pipes
|  | L-shaped concrete platform | 10" deep
|  | resurfacing | (perimeter of platform, trench)
20000
UPGRADE OF DUST EXTRACTION SYSTEM
|  | chipper |  |  | 45000
|  | chipper connection to overhead duct |  |  | 5000
|  | retrofit of dust extraction system | hopper replacement/retrofit |  | 10000
|  | auger from dust extraction hopper to silo | 28 m (92') |  | 10000
70000
FUEL STORAGE
|  | silo | 950 cft |  | 18000
|  | silo installation |  |  | 4000
22000
FIREBOX BOILER
|  | firebox boiler, incl. | 250 kW |  | 120000
fuel extraction system for silo
auger from silo to combustor
rotary air lock
stoker screw
deluge system / emergency fuel cut-off
flue gas recirc.
automatic deashing
ash hopper
pneumatic soot blower
safety valves
boiler bypass incl. 3-way valve
120000
FLUEGAS TREATMENT
|  | particulate filter | PM < 18mg/sm³ |  | 85000
|  | Chimney | 40' insulated, incl. guy wires |  | 20000
105000
INSTALLATION
|  | electrical installation |  |  | 10000
|  | installation inside container | 40' hi-cube incl 2 doors |  | 45000
|  | heating installation, incl. |  |  | 15000
T from ring pipeline to heat exchanger
|  | heat exchanger | 250 kW |  | 4000
|  | all valves downstream of boiler bypass |  |  | 1000
|  | pipes | 3" |  | 1000
|  | heat meter |  |  | 1500
|  | system main pump |  |  | 2000
|  | crane rental |  |  | 1000
|  | container shipment |  |  | 5000
85500
ENGINEERING
|  | building permit |  |  | 2000
|  | mechanical engineering | excl geo-tech |  | 5000
|  | heating engineering |  |  | 6000
|  | stack tester |  |  | 2000
|  | coordinating engineer |  |  | 5000
20000
| SUB-TOTAL |  | excl. HST |  |  | 442500
| contingencies |  | 20% |  | 88500
| HST *(Estimate after higher education credit.) |  | 4% |  | 17700
| Total Capital Cost |  |  |  |  | 548700
Operation and Maintenance Cost
| Fixed O&M Costs |  |  | Total hours/yr | Rate ($/hour) | Total
| staffing cost during operation | 1 | hour per day | 365 | 35 | 12775
| displaced staffing cost (existing cost to empty old 6 bins of old dust extraction unit) | -0.75 | hour per day | -273.75 | 35 | -9581.25
| grates, ash and container cleanup | 4 | hours per 2-week period | 104 | 35 | 3640
| filter & boiler tube cleaning | 8 | hours per 4-week period | 104 | 35 | 3640
| total annual staffing costs |  | Total hours per year: | 299.25 |  | 10473.75 | per year
Variable O&M Costs
| ash dumping (1% of tbd) | 1% | tonne per year | 3 | 50 | 150 | per year
| electricity consumption |  | kWh/yr (incl chipper) | 1000 | 0.0393 | 39.3 | per year
| variable maintenance cost (due to hrs of operation) | [included in fixed cost - assuming boiler is running at full capacity] |  |  |  | 0
| total variable O&M costs |  |  |  |  | 189.3 | per year
| TOTAL O&M costs |  |  |  |  | 10663.05 | per year

## My Project Savings
My Project Savings
Note the reader of this example:
This is an example only. The numbers in this section might not reflect perfectly a real life project. The intention is to illustrate what sort of calculations are needed to apply to the BCIT Sustainability revolving fund.
| : | Fixed numbers used in the various calculations
| : | Enter your own project figures here
| : | Automatically calculated figures
What we have…
|  | Figure | Unit | Comments
| Amount of wood per yr: | 265000 | kg
| Energy Available in wood: | 4500 | GJ | This is the equivalent of how much Natural Gas will be displaced
| Greenhouse Gas emission avoided: | 250 | tonnes of CO2eq | From BCIT GHG Calculator (.xls); from GJ of Natural Gas displaced
|  | Figure | Unit | Comments
| Electricity rate: | 0.068 | $/kWh
| Natural Gas rate: | 9 | $/GJ
| Greenhouse Gas emissions Carbon offset cost: | 25 | $/tonne of CO2 equivalent
Calculations of savings...
|  | Figure | Unit | Comments
| "Free" energy from our own wood waste [and avoided natural gas purchase]: | 40500 | $/yr
| Greenhouse Gas Emissions Savings: | 6250 | $/yr
| Electrical savings: | 0 | $/yr
| Water Savings: | 0 | $/yr
| Avoided tipping/hauling fee: | 12000 | $/yr
| Total $ savings: | 58750 | $/yr
Note:
The above calculation is a sound analysis based on solid theory. It is important to note that applicants to the BCIT Sustainability Revolving Fund will have to prove that the savings are real and happening during the entire duration of the loan (until fully reimbursed). The methodology selected to do this demonstration will have to be documented in the application form.

## NPV Calculation
Total Life Cycle Net Present Value
Note to the reader: this tab automatically calculates the Total Life Cycle Net Present Value and reports it in the summary tab. This is why it was made invisible (Hidden).
Costs for Period (yr) | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Capital investment
Total Capital Cost | 548700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Incentives
Total that will be received for this project (grants) | -250000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Operation and Maintenance Cost
Total Ops & Maintenance (annual) | 0 | 10663.05 | 10876.311 | 11093.8372 | 11315.714 | 11542.0282 | 11772.8688 | 12008.3262 | 12248.4927 | 12493.4626 | 12743.3318 | 12998.1985 | 13258.1624 | 13523.3257 | 13793.7922 | 14069.668 | 14351.0614 | 14638.0826 | 14930.8443 | 15229.4612 | 15534.0504
Total Costs | 298700 | 10663.05 | 10876.311 | 11093.8372 | 11315.714 | 11542.0282 | 11772.8688 | 12008.3262 | 12248.4927 | 12493.4626 | 12743.3318 | 12998.1985 | 13258.1624 | 13523.3257 | 13793.7922 | 14069.668 | 14351.0614 | 14638.0826 | 14930.8443 | 15229.4612 | 15534.0504
Savings for Period (yr) | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Bundles savings | 0 | 58750 | 59925 | 61123.5 | 62345.97 | 63592.8894 | 64864.7472 | 66162.0421 | 67485.283 | 68834.9886 | 70211.6884 | 71615.9222 | 73048.2406 | 74509.2054 | 75999.3895 | 77519.3773 | 79069.7649 | 80651.1602 | 82264.1834 | 83909.467 | 85587.6564
Total Savings | 0 | 58750 | 59925 | 61123.5 | 62345.97 | 63592.8894 | 64864.7472 | 66162.0421 | 67485.283 | 68834.9886 | 70211.6884 | 71615.9222 | 73048.2406 | 74509.2054 | 75999.3895 | 77519.3773 | 79069.7649 | 80651.1602 | 82264.1834 | 83909.467 | 85587.6564
Period (yr) | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Net Cash Flow | -298700 | 48086.95 | 49048.689 | 50029.6628 | 51030.256 | 52050.8612 | 53091.8784 | 54153.7159 | 55236.7903 | 56341.5261 | 57468.3566 | 58617.7237 | 59790.0782 | 60985.8798 | 62205.5974 | 63449.7093 | 64718.7035 | 66013.0776 | 67333.3391 | 68680.0059 | 70053.606
Net Project Value | -298700 | -250613.05 | -201564.361 | -151534.6982 | -100504.4422 | -48453.581 | 4638.2974 | 58792.0133 | 114028.8036 | 170370.3296 | 227838.6862 | 286456.41 | 346246.4882 | 407232.3679 | 469437.9653 | 532887.6746 | 597606.3781 | 663619.4556 | 730952.7947 | 799632.8006 | 869686.4067
Period (yr) | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
Discounted Cash Flow | -298700 | 45365.0472 | 43653.1586 | 42005.8696 | 40420.7424 | 38895.4314 | 37427.6793 | 36015.314 | 34656.2456 | 33348.4627 | 32090.0302 | 30879.0856 | 29713.8371 | 28592.5602 | 27513.5957 | 26475.3468 | 25476.2771 | 24514.9082 | 23589.8173 | 22699.6355 | 21843.0455
Discounted Cash Flow (with If formula to take into account life span entered in Summary tab) | -298700 | 45365.0472 | 43653.1586 | 42005.8696 | 40420.7424 | 38895.4314 | 37427.6793 | 36015.314 | 34656.2456 | 33348.4627 | 32090.0302 | 30879.0856 | 29713.8371 | 28592.5602 | 27513.5957 | 26475.3468 | 25476.2771 | 24514.9082 | 23589.8173 | 22699.6355 | 21843.0455
| Total Life Cycle Net Present Value | 346476.09