## Market Baseline (no VFD)
Baseline Design
Energy Consumption Calculation
System information
This worksheet if for BC Hydro Custom Incentive Program (CIP) purposes only.
The CIP is interested in understanding the kWh savings going from a base case using motors meeting ASHRAE 90.1 - 2004 High Efficiency Standard to the solution proposed by BCIT.
The system described below represents the base case per BC Hydro's definition:
Run when requested by instructor usually between 6am – 10pm (No VFD; On or Off)
Hours of operation in a day: |  | 15 | hrs/day [is actually 16 hrs except on Saturday when it is 8 hrs - using 15 hrs/day slightly corrects the data while keeping this xls sheet simple]
Number of days per week: |  | 6 | days/week
Number of weeks per year: |  | 50 | weeks/yr
Number of operating hours per year: |  | 4500 | hrs/yr
EF #1 | No VFD | 40 | hp
EF #2a | No VFD | 25 | hp
EF #2b | No VFD | 25 | hp
EF #3 | No VFD | 40 | hp
EF #4 | No VFD | 25 | hp
EF #5 | No VFD | 20 | hp
EF #6 | No VFD | 10 | hp
EF #7 | No VFD | 5 | hp
SF #1 (MUA) | No VFD | 25 | hp
SF #2 (MUA) | No VFD | 25 | hp
SF #3 (MUA) | No VFD | 25 | hp
SF #4 (MUA) | No VFD | 25 | hp
SF #5 (MUA) | No VFD | 30 | hp
Grinding Room EF #1 | No VFD | 15 | hp
Grinding Room EF #2 | No VFD | 15 | hp
Reference Data - Motor Efficiencies
[Note 1: The data below is use in the kWh savings calculation shown in subsequent sections - These are the figures recommended by BCH Power Smart Engineering]
| HP | High Eff*
| 0.17021 | 55%
| 0.05 | 55%
| 0.1 | 55%
| 0.125 | 55%
| 0.14286 | 55%
| 0.16667 | 55%
| 0.25 | 60%
| 0.33 | 60%
| 0.5 | 70%
| 0.75 | 84%
| 0.83333 | 84%
| 1 | 82.5%
| 1.5 | 84%
| 2 | 84%
| 3 | 87.5%
| 4 | 87.5%
| 5 | 87.5%
| 5.5 | 87.5%
| 7.5 | 89.5%
| 10 | 89.5%
| 15 | 91%
| 20 | 91%
| 25 | 92.4%
| 30 | 92.4%
| 40 | 93%
| 50 | 93%
| 60 | 93.6%
| 70 | 93.9% | from extrapolation
| 75 | 94.1%
| 90 | 94.4% | from extrapolation
| 100 | 94.5%
| 125 | 94.5%
| 150 | 95%
| 175 | 95%
| 200 | 95%
Specs for the baseline system
Formula: | kW = hp x 0.746 x Load Factor / Efficiency
With Load Factor recommended by BCH for this kind of calculation:
LF: | 80.5%
| hp | Eff. | kW | Hours of Operation (hrs/yr) | kWh/yr
EF #1 | 40 | 93% | 25.8292 | 4500 | 116231.6129
EF #2a | 25 | 92.4% | 16.2481 | 4500 | 73116.4773
EF #2b | 25 | 92.4% | 16.2481 | 4500 | 73116.4773
EF #3 | 40 | 93% | 25.8292 | 4500 | 116231.6129
EF #4 | 25 | 92.4% | 16.2481 | 4500 | 73116.4773
EF #5 | 20 | 91% | 13.1985 | 4500 | 59393.0769
EF #6 | 10 | 89.5% | 6.7098 | 4500 | 30194.2458
EF #7 | 5 | 87.5% | 3.4316 | 4500 | 15442.2
DC #1 | 15 | 91% | 9.8988 | 4500 | 44544.8077
DC #2 | 15 | 91% | 9.8988 | 4500 | 44544.8077
SF #1 (MUA) | 25 | 92.4% | 16.2481 | 4500 | 73116.4773
SF #2 (MUA) | 25 | 92.4% | 16.2481 | 4500 | 73116.4773
SF #3 (MUA) | 25 | 92.4% | 16.2481 | 4500 | 73116.4773
SF #4 (MUA) | 25 | 92.4% | 16.2481 | 4500 | 73116.4773
SF #5 (MUA) | 30 | 92.4% | 19.4977 | 4500 | 87739.7727
|  | Total: | 228.0306 | Total: | 1026137.4776
Annual electricity consumption:
| kWh: | 1026137.4776

## Proposed (with VFD)
Proposed Design
Energy Consumption Calculation
System information
Same design as "Market Baseline" except VFD are used where indicated.
Reference Data - Motor Efficiencies
Note:
BC Hydro recommends using the table below to estimate annual energy use by entering the estimated % time that the VFD will run at a certain speed.
Please note that “new kW” calculation is using a more conservative “square law” instead of “cube law”.
Exhaust air: | [7 empty] | Supply air:
EF #1 | [7 empty] | SF #1 (MUA)
Motor HP | 40 |  | Hr/day | 15 |  |  |  | Motor HP | 25 |  | Hr/day | 15
Motor Eff | 93% |  | Days/wk | 6 |  |  |  | Motor Eff | 92.4% |  | Days/wk | 6
VFD Eff | 97% |  | Hr/wk | 90 |  |  |  | VFD Eff | 97% |  | Hr/wk | 90
kW | 25.8292 |  | Wk/yr | 50 |  |  |  | kW | 16.2481 |  | Wk/yr | 50
|  |  | Annual hrs | 4500 | [6 empty] | Annual hrs | 4500
VFD speed | % time | Hr | New kW | kWh |  |  |  | VFD speed | % time | Hr | New kW | kWh
100% | 10% | 450 | 25.8292 | 11623.1613 |  |  |  | 100% | 10% | 450 | 16.2481 | 7311.6477
90% | 0% | 0 | 20.9217 | 0 |  |  |  | 90% | 0% | 0 | 13.161 | 0
80% | 10% | 450 | 16.5307 | 7438.8232 |  |  |  | 80% | 10% | 450 | 10.3988 | 4679.4545
70% | 0% | 0 | 12.6563 | 0 |  |  |  | 70% | 0% | 0 | 7.9616 | 0
60% | 0% | 0 | 9.2985 | 0 |  |  |  | 60% | 0% | 0 | 5.8493 | 0
50% | 40% | 1800 | 6.4573 | 11623.1613 |  |  |  | 50% | 40% | 1800 | 4.062 | 7311.6477
40% | 0% | 0 | 4.1327 | 0 |  |  |  | 40% | 0% | 0 | 2.5997 | 0
30% | 40% | 1800 | 2.3246 | 4184.3381 |  |  |  | 30% | 40% | 1800 | 1.4623 | 2632.1932
20% | 0% | 0 | 1.0332 | 0 |  |  |  | 20% | 0% | 0 | 0.64992 | 0
10% | 0% | 0 | 0.25829 | 0 |  |  |  | 10% | 0% | 0 | 0.16248 | 0
Total | 100% | 4500 |  | 34869.4839 | Average kW: | 7.7488 |  | Total | 100% | 4500 |  | 21934.9432 | Average kW: | 4.8744
EF #2a | [7 empty] | SF #2 (MUA)
Motor HP | 25 |  | Hr/day | 15 |  |  |  | Motor HP | 25 |  | Hr/day | 15
Motor Eff | 92.4% |  | Days/wk | 6 |  |  |  | Motor Eff | 92.4% |  | Days/wk | 6
VFD Eff | 97% |  | Hr/wk | 90 |  |  |  | VFD Eff | 97% |  | Hr/wk | 90
kW | 16.2481 |  | Wk/yr | 50 |  |  |  | kW | 16.2481 |  | Wk/yr | 50
|  |  | Annual hrs | 4500 | [6 empty] | Annual hrs | 4500
VFD speed | % time | Hr | New kW | kWh |  |  |  | VFD speed | % time | Hr | New kW | kWh
100% | 10% | 450 | 16.2481 | 7311.6477 |  |  |  | 100% | 10% | 450 | 16.2481 | 7311.6477
90% | 0% | 0 | 13.161 | 0 |  |  |  | 90% | 0% | 0 | 13.161 | 0
80% | 10% | 450 | 10.3988 | 4679.4545 |  |  |  | 80% | 10% | 450 | 10.3988 | 4679.4545
70% | 0% | 0 | 7.9616 | 0 |  |  |  | 70% | 0% | 0 | 7.9616 | 0
60% | 0% | 0 | 5.8493 | 0 |  |  |  | 60% | 0% | 0 | 5.8493 | 0
50% | 40% | 1800 | 4.062 | 7311.6477 |  |  |  | 50% | 40% | 1800 | 4.062 | 7311.6477
40% | 0% | 0 | 2.5997 | 0 |  |  |  | 40% | 0% | 0 | 2.5997 | 0
30% | 40% | 1800 | 1.4623 | 2632.1932 |  |  |  | 30% | 40% | 1800 | 1.4623 | 2632.1932
20% | 0% | 0 | 0.64992 | 0 |  |  |  | 20% | 0% | 0 | 0.64992 | 0
10% | 0% | 0 | 0.16248 | 0 |  |  |  | 10% | 0% | 0 | 0.16248 | 0
Total | 100% | 4500 |  | 21934.9432 | Average kW: | 4.8744 |  | Total | 100% | 4500 |  | 21934.9432 | Average kW: | 4.8744
EF #2b
Motor HP | 25 |  | Hr/day | 15
Motor Eff | 92.4% |  | Days/wk | 6
VFD Eff | 97% |  | Hr/wk | 90
kW | 16.2481 |  | Wk/yr | 50
|  |  | Annual hrs | 4500
VFD speed | % time | Hr | New kW | kWh
100% | 10% | 450 | 16.2481 | 7311.6477
90% | 0% | 0 | 13.161 | 0
80% | 10% | 450 | 10.3988 | 4679.4545
70% | 0% | 0 | 7.9616 | 0
60% | 0% | 0 | 5.8493 | 0
50% | 40% | 1800 | 4.062 | 7311.6477
40% | 0% | 0 | 2.5997 | 0
30% | 40% | 1800 | 1.4623 | 2632.1932
20% | 0% | 0 | 0.64992 | 0
10% | 0% | 0 | 0.16248 | 0
Total | 100% | 4500 |  | 21934.9432 | Average kW: | 4.8744
EF #3 | [7 empty] | SF #3 (MUA)
Motor HP | 40 |  | Hr/day | 15 |  |  |  | Motor HP | 25 |  | Hr/day | 15
Motor Eff | 93% |  | Days/wk | 6 |  |  |  | Motor Eff | 92.4% |  | Days/wk | 6
VFD Eff | 97% |  | Hr/wk | 90 |  |  |  | VFD Eff | 97% |  | Hr/wk | 90
kW | 25.8292 |  | Wk/yr | 50 |  |  |  | kW | 16.2481 |  | Wk/yr | 50
|  |  | Annual hrs | 4500 | [6 empty] | Annual hrs | 4500
VFD speed | % time | Hr | New kW | kWh |  |  |  | VFD speed | % time | Hr | New kW | kWh
100% | 10% | 450 | 25.8292 | 11623.1613 |  |  |  | 100% | 10% | 450 | 16.2481 | 7311.6477
90% | 0% | 0 | 13.161 | 0 |  |  |  | 90% | 0% | 0 | 13.161 | 0
80% | 10% | 450 | 10.3988 | 4679.4545 |  |  |  | 80% | 10% | 450 | 10.3988 | 4679.4545
70% | 0% | 0 | 7.9616 | 0 |  |  |  | 70% | 0% | 0 | 7.9616 | 0
60% | 0% | 0 | 5.8493 | 0 |  |  |  | 60% | 0% | 0 | 5.8493 | 0
50% | 40% | 1800 | 4.062 | 7311.6477 |  |  |  | 50% | 40% | 1800 | 4.062 | 7311.6477
40% | 0% | 0 | 2.5997 | 0 |  |  |  | 40% | 0% | 0 | 2.5997 | 0
30% | 40% | 1800 | 1.4623 | 2632.1932 |  |  |  | 30% | 40% | 1800 | 1.4623 | 2632.1932
20% | 0% | 0 | 0.64992 | 0 |  |  |  | 20% | 0% | 0 | 0.64992 | 0
10% | 0% | 0 | 0.16248 | 0 |  |  |  | 10% | 0% | 0 | 0.16248 | 0
Total | 100% | 4500 |  | 26246.4567 | Average kW: | 5.8325 |  | Total | 100% | 4500 |  | 21934.9432 | Average kW: | 4.8744
EF #4 | [7 empty] | SF #4 (MUA)
Motor HP | 25 |  | Hr/day | 15 |  |  |  | Motor HP | 25 |  | Hr/day | 15
Motor Eff | 92.4% |  | Days/wk | 6 |  |  |  | Motor Eff | 92.4% |  | Days/wk | 6
VFD Eff | 97% |  | Hr/wk | 90 |  |  |  | VFD Eff | 97% |  | Hr/wk | 90
kW | 16.2481 |  | Wk/yr | 50 |  |  |  | kW | 16.2481 |  | Wk/yr | 50
|  |  | Annual hrs | 4500 | [6 empty] | Annual hrs | 4500
VFD speed | % time | Hr | New kW | kWh |  |  |  | VFD speed | % time | Hr | New kW | kWh
100% | 10% | 450 | 16.2481 | 7311.6477 |  |  |  | 100% | 10% | 450 | 16.2481 | 7311.6477
90% | 0% | 0 | 13.161 | 0 |  |  |  | 90% | 0% | 0 | 13.161 | 0
80% | 10% | 450 | 10.3988 | 4679.4545 |  |  |  | 80% | 10% | 450 | 10.3988 | 4679.4545
70% | 0% | 0 | 7.9616 | 0 |  |  |  | 70% | 0% | 0 | 7.9616 | 0
60% | 0% | 0 | 5.8493 | 0 |  |  |  | 60% | 0% | 0 | 5.8493 | 0
50% | 40% | 1800 | 4.062 | 7311.6477 |  |  |  | 50% | 40% | 1800 | 4.062 | 7311.6477
40% | 0% | 0 | 2.5997 | 0 |  |  |  | 40% | 0% | 0 | 2.5997 | 0
30% | 40% | 1800 | 1.4623 | 2632.1932 |  |  |  | 30% | 40% | 1800 | 1.4623 | 2632.1932
20% | 0% | 0 | 0.64992 | 0 |  |  |  | 20% | 0% | 0 | 0.64992 | 0
10% | 0% | 0 | 0.16248 | 0 |  |  |  | 10% | 0% | 0 | 0.16248 | 0
Total | 100% | 4500 |  | 21934.9432 | Average kW: | 4.8744 |  | Total | 100% | 4500 |  | 21934.9432 | Average kW: | 4.8744
EF #6
Motor HP | 10 |  | Hr/day | 15
Motor Eff | 89.5% |  | Days/wk | 6
VFD Eff | 97% |  | Hr/wk | 90
kW | 6.7098 |  | Wk/yr | 50
|  |  | Annual hrs | 4500
VFD speed | % time | Hr | New kW | kWh
100% | 10% | 450 | 6.7098 | 3019.4246
90% | 0% | 0 | 5.435 | 0
80% | 10% | 450 | 4.2943 | 1932.4317
70% | 0% | 0 | 3.2878 | 0
60% | 0% | 0 | 2.4155 | 0
50% | 40% | 1800 | 1.6775 | 3019.4246
40% | 0% | 0 | 1.0736 | 0
30% | 40% | 1800 | 0.60388 | 1086.9928
20% | 0% | 0 | 0.26839 | 0
10% | 0% | 0 | 0.067098 | 0
Total | 100% | 4500 |  | 9058.2737 | Average kW: | 2.0129
EF #7
Motor HP | 5 |  | Hr/day | 15
Motor Eff | 87.5% |  | Days/wk | 6
VFD Eff | No VFD |  | Hr/wk | 90
kW | 3.4316 |  | Wk/yr | 50
|  |  | Annual hrs | 4500
VFD speed | % time | Hr | New kW | kWh
100% | 100% | 4500 | 3.4316 | 15442.2
90% | 0% | 0 | 2.7796 | 0
80% | 0% | 0 | 2.1962 | 0
70% | 0% | 0 | 1.6815 | 0
60% | 0% | 0 | 1.2354 | 0
50% | 0% | 0 | 0.8579 | 0
40% | 0% | 0 | 0.54906 | 0
30% | 0% | 0 | 0.30884 | 0
20% | 0% | 0 | 0.13726 | 0
10% | 0% | 0 | 0.034316 | 0
Total | 100% | 4500 |  | 15442.2 | Average kW: | 3.4316
EF #5 | [7 empty] | SF #5 (MUA)
Motor HP | 20 |  | Hr/day | 15 |  |  |  | Motor HP | 30 |  | Hr/day | 15
Motor Eff | 91% |  | Days/wk | 6 |  |  |  | Motor Eff | 92.4% |  | Days/wk | 6
VFD Eff | 97% |  | Hr/wk | 90 |  |  |  | VFD Eff | 97% |  | Hr/wk | 90
kW | 13.1985 |  | Wk/yr | 50 |  |  |  | kW | 19.4977 |  | Wk/yr | 50
|  |  | Annual hrs | 4500 | [6 empty] | Annual hrs | 4500
VFD speed | % time | Hr | New kW | kWh |  |  |  | VFD speed | % time | Hr | New kW | kWh
100% | 10% | 450 | 13.1985 | 5939.3077 |  |  |  | 100% | 10% | 450 | 19.4977 | 8773.9773
90% | 0% | 0 | 10.6908 | 0 |  |  |  | 90% | 0% | 0 | 15.7932 | 0
80% | 10% | 450 | 8.447 | 3801.1569 |  |  |  | 80% | 10% | 450 | 12.4785 | 5615.3455
70% | 0% | 0 | 6.4672 | 0 |  |  |  | 70% | 0% | 0 | 9.5539 | 0
60% | 0% | 0 | 4.7514 | 0 |  |  |  | 60% | 0% | 0 | 7.0192 | 0
50% | 40% | 1800 | 3.2996 | 5939.3077 |  |  |  | 50% | 40% | 1800 | 4.8744 | 8773.9773
40% | 0% | 0 | 2.1118 | 0 |  |  |  | 40% | 0% | 0 | 3.1196 | 0
30% | 40% | 1800 | 1.1879 | 2138.1508 |  |  |  | 30% | 40% | 1800 | 1.7548 | 3158.6318
20% | 0% | 0 | 0.52794 | 0 |  |  |  | 20% | 0% | 0 | 0.77991 | 0
10% | 0% | 0 | 0.13198 | 0 |  |  |  | 10% | 0% | 0 | 0.19498 | 0
Total | 100% | 4500 | #VALUE! | 17817.9231 | Average kW: | 3.9595 |  | Total | 100% | 4500 |  | 26321.9318 | Average kW: | 5.8493
DC #1
Motor HP | 15 |  | Hr/day | 15
Motor Eff | 91% |  | Days/wk | 6
VFD Eff | 97% |  | Hr/wk | 90
kW | 9.8988 |  | Wk/yr | 50
|  |  | Annual hrs | 4500
VFD speed | % time | Hr | New kW | kWh
100% | 10% | 450 | 9.8988 | 4454.4808
90% | 0% | 0 | 8.0181 | 0
80% | 10% | 450 | 6.3353 | 2850.8677
70% | 0% | 0 | 4.8504 | 0
60% | 0% | 0 | 3.5636 | 0
50% | 40% | 1800 | 2.4747 | 4454.4808
40% | 0% | 0 | 1.5838 | 0
30% | 40% | 1800 | 0.8909 | 1603.6131
20% | 0% | 0 | 0.39595 | 0
10% | 0% | 0 | 0.098988 | 0
Total | 100% | 4500 |  | 13363.4423 | Average kW: | 2.9697
DC #2
Motor HP | 15 |  | Hr/day | 15
Motor Eff | 91% |  | Days/wk | 6
VFD Eff | 97% |  | Hr/wk | 90
kW | 9.8988 |  | Wk/yr | 50
|  |  | Annual hrs | 4500
VFD speed | % time | Hr | New kW | kWh
100% | 10% | 450 | 9.8988 | 4454.4808
90% | 0% | 0 | 8.0181 | 0
80% | 10% | 450 | 6.3353 | 2850.8677
70% | 0% | 0 | 4.8504 | 0
60% | 0% | 0 | 3.5636 | 0
50% | 40% | 1800 | 2.4747 | 4454.4808
40% | 0% | 0 | 1.5838 | 0
30% | 40% | 1800 | 0.8909 | 1603.6131
20% | 0% | 0 | 0.39595 | 0
10% | 0% | 0 | 0.098988 | 0
Total | 100% | 4500 |  | 13363.4423 | Average kW: | 2.9697
Average kW | 43.548 | kW (all unites combined) | [5 empty] | Average kW | 25.347 | kW (all unites combined)
[5 empty] | 68.8951 | kWh/yr | for All Units combined
Total energy consumption for Exhaust: | 195966.0516 | kWh/yr | for All Units combined |  |  |  |  | Total energy consumption for Return: | 114061.7045 | kWh/yr | for All Units combined
Total energy consumption for Exhaust and Return:
[5 empty] | 310027.7561 | kWh/yr | for All Units combined
Notes: VFD efficiency note included.

## Energy Savings (base-proposed)
Energy Savings (base-proposed)
Market Baseline (no VFD)
Total electricity consumption | 1026137.4776 | kWh/yr
Proposed (with VFD)
Total electricity consumption | 310027.7561 | kWh/yr
Calculated Electrical Savings
Total electricity conserved | 716109.7214 | kWh/yr
Demand Savings
Market Baseline (no VFD)
Total Demand | 228.0306 | kW
Proposed (with VFD)
Average demand | 68.8951 | kW
Calculated Electrical Savings
Demand savings (average) | 159.1355 | kW

## Incremental Cost
Incremental Cost associated to the Energy Efficient Proposed Case
VFDs
What | Incremental Cost ($)
Material | 61556.56
Labor (installation) | 20000
DDC package
What | Incremental Cost ($)
Material and Labor (installation) | 133114
Extraction Arms (with auto dampers, current sensors and damper controls)
What | Incremental Cost ($)
Material | 137038.56
Labor (installation) | 85000
Custom Design Welding Booth Hood
What | Incremental Cost ($)
Material | 18000
Labor (installation) | 25000
Controls associated to AHU
What | Incremental Cost ($)
Material | 5000
Labor (installation) | 30000
Total Incremental Cost* | 514709.12
*: the costs above come from a mix of quotes and estimates (typically: quotes for parts, estimates for labor)