## Savings
Gas Saving Calculations
Q = CFM * Heat Capacity * Delta T
| 100000 | CFM
| 11.7327 | Avergae HDD (K)
| 1.2 | Air Density at 20 deg C (kg/m3)
| 0.0283 | Concersion CFM to CMM (m3/ft3)
| 1 | Heat Capacity (KJ/kg*K
Q= | 39844.1584
Run time
| 15 | hrs/day
| 6 | days/wk
| 41 | wks/yr
| 60 | min/hr
Total Run time = | 221400
Energy | 8821496673.2673 | KJ
| 8821.4967 | GJ

## HDD
Description: | Celsius-based 5-year-average (2009 to 2013) heating degree days for a base temperature of 20.0C
Source: | www.degreedays.net (using temperature data from www.wunderground.com)
Accuracy: | Estimates were made to account for missing data: the "% Estimated" column shows how much each figure was affected (0% is best, 100% is worst)
Station: | Vancouver International Air-Port, B. C., BC, CA (123.17W,49.18N)
Station ID: | CYVR
| HDD | % Estimated
Jan | 495 | 0.04
Feb | 423 | 0.01
Mar | 420 | 0.02
Apr | 330 | 0.04
May | 239 | 0.08
Jun | 139 | 0.03
Sep | 138 | 0.07
Oct | 302 | 0.07
Nov | 412 | 0.05
Dec | 507 | 0.06
Total | 3555 | 0.06
Average per day | 11.7327

## CFMs
Pre-retrofit | 145380 | ft3/min
Post-retrofit design capacity | 92200 | ft3/min
VFD average speed | 50%
Post-retrofit operation | 46100 | ft3/min
Reduction | 99280 | ft3/min