## Natural Gas
Measurement and Verification
Welding Ventilation Energy Efficient Upgrade
Natural Gas
Meter Name | Meter Type | Reading Start | Reading End | Reading Length | Consumption | Units | HDD at 15.5C* | HDD at 15.5C [partially corrected for reading period]
Submeter-GAS-NE08 | Natural Gas | 2011-01-05 | 2011-02-02 23:59 | 29 | 1425 | GJ | n/a | n/a
Submeter-GAS-NE08 | Natural Gas | 2011-02-03 | 2011-03-01 23:59 | 27 | 1568 | GJ | n/a | n/a
Submeter-GAS-NE08 | Natural Gas | 2011-03-02 | 2011-04-01 23:59 | 31 | 1488 | GJ | n/a | n/a
Submeter-GAS-NE08 | Natural Gas | 2011-04-02 | 2011-05-03 23:59 | 32 | 1372.8199 | GJ | n/a | n/a
Submeter-GAS-NE08 | Natural Gas | 2011-05-04 | 2011-06-03 23:59 | 31 | 725.13 | GJ | n/a | n/a
Submeter-GAS-NE08 | Natural Gas | 2011-06-04 | 2011-07-06 23:59 | 33 | 61.21 | GJ | n/a | n/a
Submeter-GAS-NE08 | Natural Gas | 2011-07-07 | 2011-08-05 23:59 | 30 | 16.87 | GJ | n/a | n/a
Submeter-GAS-NE08 | Natural Gas | 2011-08-06 | 2011-09-02 23:59 | 28 | 11.47 | GJ | n/a | n/a
Submeter-GAS-NE08 | Natural Gas | 2011-09-03 | 2011-10-04 23:59 | 32 | 55.58 | GJ | n/a | n/a
Submeter-GAS-NE08 | Natural Gas | 2011-10-05 | 2011-11-15 23:59 | 42 | 1083.54 | GJ | n/a | n/a
Submeter-GAS-NE08 | Natural Gas | 2011-11-16 | 2011-12-12 23:59 | 27 | 1488.86 | GJ | n/a | n/a
Submeter-GAS-NE08 | Natural Gas | 2011-12-13 | 2012-01-05 23:59 | 24 | 1276.91 | GJ | n/a | n/a
|  |  |  | N: | 12
|  |  |  | Total: | 10573.39 | GJ
|  |  |  | Average: | 881.1158 | GJ
|  |  |  | Reading Length | Consumption | Units | HDD at 15.5C* | HDD at 15.5C [partially corrected for reading period]
Submeter-GAS-NE08 | Natural Gas | 2012-01-06 | 2012-02-06 23:59 | 32 | 1798.8 | GJ | 370 | 381.9355
Submeter-GAS-NE08 | Natural Gas | 2012-02-07 | 2012-03-01 23:59 | 24 | 1146.09 | GJ | 307 | 263.1429
Submeter-GAS-NE08 | Natural Gas | 2012-03-02 | 2012-04-04 23:59 | 34 | 1469.95 | GJ | 303 | 332.3226
Submeter-GAS-NE08 | Natural Gas | 2012-04-05 | 2012-05-01 23:59 | 27 | 743.11 | GJ | 180 | 162
Submeter-GAS-NE08 | Natural Gas | 2012-05-02 | 2012-06-06 23:59 | 36 | 647.8 | GJ | 108 | 125.4194
Submeter-GAS-NE08 | Natural Gas | 2012-06-07 | 2012-07-04 23:59 | 28 | 109.64 | GJ | 56 | 52.2667
Submeter-GAS-NE08 | Natural Gas | 2012-07-05 | 2012-08-01 23:59 | 28 | 0.37 | GJ | 13 | 11.7419
Submeter-GAS-NE08 | Natural Gas | 2012-08-02 | 2012-09-05 23:59 | 35 | 0.22 | GJ | 7 | 7.9032
Submeter-GAS-NE08 | Natural Gas | 2012-09-06 | 2012-10-01 23:59 | 26 | 0.97 | GJ | 39 | 33.8
Submeter-GAS-NE08 | Natural Gas | 2012-10-02 | 2012-11-02 23:59 | 32 | 645.23 | GJ | 159 | 164.129
Submeter-GAS-NE08 | Natural Gas | 2012-11-03 | 2012-11-29 23:59 | 27 | 978.07 | GJ | 244 | 219.6
Submeter-GAS-NE08 | Natural Gas | 2012-11-30 | 2013-01-03 23:59 | 35 | 1661.8 | GJ | 342 | 386.129
|  |  |  | N: | 12 |  | 12 | 12
|  |  |  | Total: | 9202.05 | GJ | 2128 | 2140.3902
|  |  |  | Average: | 766.8375 | GJ
Submeter-GAS-NE08 | Natural Gas | 2013-01-04 | 2013-02-04 23:59 | 32 | 1685.1801 | GJ | Data excluded as during construction |  |  |  |  | Equation parameters:
Submeter-GAS-NE08 | Natural Gas | 2013-02-05 | 2013-03-04 23:59 | 28 | 1111.3199 | GJ | [5 empty] | x: | 4.7
Submeter-GAS-NE08 | Natural Gas | 2013-03-05 | 2013-04-03 23:59 | 30 | 874.09 | GJ | [5 empty] | b: | -70
Submeter-GAS-NE08 | Natural Gas | 2013-04-04 | 2013-05-02 23:59 | 29 | 363.07 | GJ
Submeter-GAS-NE08 | Natural Gas | 2013-05-03 | 2013-06-03 23:59 | 32 | 69.25 | GJ
Submeter-GAS-NE08 | Natural Gas | 2013-06-04 | 2013-07-04 23:59 | 31 | 0.039999 | GJ
Submeter-GAS-NE08 | Natural Gas | 2013-07-05 | 2013-08-06 23:59 | 33 | 0.52 | GJ
Submeter-GAS-NE08 | Natural Gas | 2013-08-07 | 2013-09-05 23:59 | 30 | 0.11 | GJ
|  |  |  | Reading Length | Consumption | Units | HDD at 15.5C* | HDD at 15.5C [partially corrected for reading period] | Predicted GJ | Savings in GJ
Submeter-GAS-NE08 | Natural Gas | 2013-09-06 | 2013-10-01 23:59 | 26 | 57.67 | GJ | 38 | 32.9333 | 84.7867 | 27.1167
Submeter-GAS-NE08 | Natural Gas | 2013-10-02 | 2013-11-05 23:59 | 35 | 369.4 | GJ | 192 | 216.7742 | 948.8387 | 579.4387
Submeter-GAS-NE08 | Natural Gas | 2013-11-06 | 2013-12-02 23:59 | 27 | 399.44 | GJ | 277 | 249.3 | 1101.71 | 702.27
Submeter-GAS-NE08 | Natural Gas | 2013-12-03 | 2014-01-06 23:59 | 35 | 529.93 | GJ | 401 | 452.7419 | 2057.8871 | 1527.9571
Submeter-GAS-NE08 | Natural Gas | 2014-01-07 | 2014-02-03 23:59 | 28 | 450.93 | GJ | 342 | 308.9032 | 1381.8452 | 930.9152
Submeter-GAS-NE08 | Natural Gas | 2014-02-04 | 2014-03-04 23:59 | 29 | 432.76 | GJ | 364 | 377 | 1701.9 | 1269.14
|  |  |  | N: | 6 |  | 6 | 6
|  |  |  | Total: | 2240.13 | GJ | 1614 | 1637.6527 |  | 5036.8376 | GJ
|  |  |  | Average: | 373.355 | GJ
Equation parameters:
Simulation of a full year post-retrofit | [11 empty] | x: | 1.06
|  |  |  | Reading Length | Consumption | Units | HDD at 15.5C* | HDD at 15.5C [partially corrected for reading period] | Predicted GJ | Savings in GJ |  | b: | 83
Submeter-GAS-NE08 | Natural Gas | 2013-09-06 | 2013-10-01 23:59 | 26 | 57.67 | GJ | 38 | 32.9333 | 84.7867 | 27.1167
Submeter-GAS-NE08 | Natural Gas | 2013-10-02 | 2013-11-05 23:59 | 35 | 369.4 | GJ | 192 | 216.7742 | 948.8387 | 579.4387
Submeter-GAS-NE08 | Natural Gas | 2013-11-06 | 2013-12-02 23:59 | 27 | 399.44 | GJ | 277 | 249.3 | 1101.71 | 702.27
Submeter-GAS-NE08 | Natural Gas | 2013-12-03 | 2014-01-06 23:59 | 35 | 529.93 | GJ | 401 | 452.7419 | 2057.8871 | 1527.9571
Submeter-GAS-NE08 | Natural Gas | 2014-01-07 | 2014-02-03 23:59 | 28 | 450.93 | GJ | 342 | 308.9032 | 1381.8452 | 930.9152
Submeter-GAS-NE08 | Natural Gas | 2014-02-04 | 2014-03-04 23:59 | 29 | 432.76 | GJ | 364 | 377 | 1701.9 | 1269.14
Submeter-GAS-NE08 | Natural Gas | 2012-03-02 | 2012-04-04 23:59 | 34 | 435.2619 | GJ | 303 | 332.3226 | 1491.9161 | 1056.6542
Submeter-GAS-NE08 | Natural Gas | 2012-04-05 | 2012-05-01 23:59 | 27 | 254.72 | GJ | 180 | 162 | 691.4 | 436.68
Submeter-GAS-NE08 | Natural Gas | 2012-05-02 | 2012-06-06 23:59 | 36 | 215.9445 | GJ | 108 | 125.4194 | 519.471 | 303.5265
Submeter-GAS-NE08 | Natural Gas | 2012-06-07 | 2012-07-04 23:59 | 28 | 138.4027 | GJ | 56 | 52.2667 | 175.6533 | 37.2507
Submeter-GAS-NE08 | Natural Gas | 2012-07-05 | 2012-08-01 23:59 | 28 | 95.4465 | GJ | 13 | 11.7419 | -14.8129 | -110.2594
Submeter-GAS-NE08 | Natural Gas | 2012-08-02 | 2012-09-05 23:59 | 35 | 91.3774 | GJ | 7 | 7.9032 | -32.8548 | -124.2323
[8 empty] | N: | 12 | 12
|  |  |  | Total: | 3471.283 |  |  | Total: | 10107.7403 | 6636.4573 | GJ
[10 empty] | 1844935.1384 | kWh
* Generated with degreedays.net

## Electricity
Measurement and Verification
Welding Ventilation Energy Efficient Upgrade
Electricity
Note: there is no cooling in NE8. Heating is 100% natural gas. No need for regression analysis kWh vs HDD or CDD,
Timestamp | Electricity (kWh)
2012-01-01
2012-02-01
2012-03-01 | 101653.4613
2012-04-01 | 122811.2637
2012-05-01 | 132296.6914
2012-06-01 | 125403.0312
2012-07-01 | 117772.6719
2012-08-01 | 124968.8516
2012-09-01 | 124257.7266
2012-10-01 | 127301.9219
2012-11-01 | 126551.3594
2012-12-01 | 118138.5
Average: | 122115.5479
2013-01-01 | 131524.2031 | Data excluded as during construction
2013-02-01 | 116488.7344
2013-03-01 | 119643.4531
2013-04-01 | 100182.2031
2013-05-01 | 58429.4219
2013-06-01 | 47756
2013-07-01 | 46446.875
2013-08-01 | 47316.2812
Timestamp | Electricity (kWh)
2013-09-01 | 48929.75
2013-10-01 | 61730.625
2013-11-01 | 57381.5625
2013-12-01 | 50288.2188
2014-01-01 | 53056.75
2014-02-01 | 52188.75
2014-03-01 | 59266.375
2014-04-01 | 52716.1562
Average: | 54444.7734
Average Monthly Savings: | 67670.7745 | kWh
Average Annual Savings | 812049.2934 | kWh
Average Annual Savings | 2921.0406 | GJ
Note: a QA test will be needed to verify amount of missing data at the 15 min. intervals used to create the montly data.

## Total Energy
Total Energy Savings
Rates Assumptions:
Natural Gas |  |  | Average 2014 cost of natural gas - North Campus Account
1844935.1384 | kWh/yr |  | 10.61 | $/GJ | (including all fees + carbon tax + carbon offset)
6636.4573 | GJ/yr |  | Average 2019 cost of natural gas - North Campus Account
70412.8123 | 2014 $/yr |  | 11.86 | $/GJ | (including all fees + carbon tax + carbon offset)
78708.384 | 2019 $/yr
Average 2014 cost of electricity
Electricity |  |  | 0.0971 | $/kWh | (including all fees + carbon tax + carbon offset)
812049.2934 | kWh/yr |  | Average 2019 cost of electricity
2921.0406 | GJ/yr |  | 0.057115 | $/kWh | (including all fees + carbon tax + carbon offset)
78849.9864 | 2014 $/yr
46380.5016 | 2019 $/yr |  | Average 2014 cost of electricity demand
|  |  | 9.95 | $/kW
Total Energy Savings |  |  | Average 2019 cost of electricity demand
2656984.4318 | kWh/yr |  | 11.6934 | $/kW
9557.498 | GJ/yr
149262.7987 | 2014 $/yr | Note: savings are higher in year 1 all 100% of reduced kWh fall in part 2 of the conservation rate (based on 3 year rolling average, 100% of reduced kWh will fall in part 1 after 3 years of operations.
125088.8856 | 2019 $/yr
Estimates for demand savings:
150 | kW | (to be verified)
1492.5 | 2014 $/yr
1754.0062 | 2019 $/yr
Total Cost Savings
150755.2987 | 2014 $/yr
126842.8917 | 2019 $/yr